## construction-pivot
Values
Row Labels | Average of U-Factor with Film [W/m2-K] | Sum of Gross Area [m2]
ASHRAE 189.1-2009 EXTWALL MASS CLIMATEZONE 7-8 | 0.08 | 2.154
ASHRAE 90.1-2007 EXTROOF IEAD CLIMATEZONE 2-8 | 0.3 | 1.415
ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 6.912
EXTSLABCARPET 4IN CLIMATEZONE 1-8 | 0.15 | 28.17
Grand Total | 0.19676 | 38.651

## constructions
Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
SURFACE 16 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 14.82 | 180 | 90 | S
SURFACE 17 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 28.06 | 270 | 90 | W
SURFACE 18 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 14.82 | 0 | 90 | N
SURFACE 15 | EXTSLABCARPET 4IN CLIMATEZONE 1-8 | 0.15 | 2.945 | 5.634 | 36.43 | 0 | 180
SURFACE 19 | ASHRAE 90.1-2007 EXTROOF IEAD CLIMATEZONE 2-8 | 0.3 | 0.273 | 0.283 | 36.43 | 0 | 0
SURFACE 1 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 8.17 | 0 | 90 | N
SURFACE 10 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 7.23 | 270 | 90 | W
SURFACE 11 | ASHRAE 189.1-2009 EXTWALL MASS CLIMATEZONE 7-8 | 0.08 | 0.34 | 0.359 | 6.42 | 270 | 90 | W
SURFACE 12 | ASHRAE 189.1-2009 EXTWALL MASS CLIMATEZONE 7-8 | 0.08 | 0.34 | 0.359 | 23.39 | 180 | 90 | S
SURFACE 13 | ASHRAE 189.1-2009 EXTWALL MASS CLIMATEZONE 7-8 | 0.08 | 0.34 | 0.359 | 2.68 | 90 | 90 | E
SURFACE 2 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 25.14 | 90 | 90 | E
SURFACE 20 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 47.05 | 90 | 90 | E
SURFACE 25 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 14.17 | 270 | 90 | W
SURFACE 27 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 12.02 | 180 | 90 | S
SURFACE 28 | ASHRAE 189.1-2009 EXTWALL MASS CLIMATEZONE 7-8 | 0.08 | 0.34 | 0.359 | 11.74 | 0 | 90 | N
SURFACE 3 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 13.51 | 180 | 90 | S
SURFACE 30 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 65.12 | 0 | 90 | N
SURFACE 31 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 8.92 | 180 | 90 | S
SURFACE 32 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 6.17 | 180 | 90 | S
SURFACE 35 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 2.86 | 0 | 90 | N
SURFACE 36 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 18.99 | 270 | 90 | W
SURFACE 37 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 3.77 | 90 | 90 | E
SURFACE 4 | ASHRAE 189.1-2009 EXTWALL MASS CLIMATEZONE 7-8 | 0.08 | 0.34 | 0.359 | 31.35 | 180 | 90 | S
SURFACE 5 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 3.77 | 270 | 90 | W
SURFACE 6 | ASHRAE 90.1-2007 EXTWALL STEELFRAME CLIMATEZONE ALT-RES 2-6 | 0.22 | 0.363 | 0.384 | 32.5 | 0 | 90 | N
SURFACE 42 | EXTSLABCARPET 4IN CLIMATEZONE 1-8 | 0.15 | 2.945 | 5.634 | 79.89 | 0 | 180
SURFACE 44 | EXTSLABCARPET 4IN CLIMATEZONE 1-8 | 0.15 | 2.945 | 5.634 | 35.48 | 0 | 180
SURFACE 45 | EXTSLABCARPET 4IN CLIMATEZONE 1-8 | 0.15 | 2.945 | 5.634 | 60.82 | 0 | 180
SURFACE 9 | EXTSLABCARPET 4IN CLIMATEZONE 1-8 | 0.15 | 2.945 | 5.634 | 41.06 | 0 | 180
SURFACE 14 | ASHRAE 90.1-2007 EXTROOF IEAD CLIMATEZONE 2-8 | 0.3 | 0.273 | 0.283 | 140.61 | 180 | 12.34
SURFACE 26 | ASHRAE 189.1-2009 EXTWALL MASS CLIMATEZONE 7-8 | 0.08 | 0.342 | 0.359 | 5.67 | 0 | 0
SURFACE 29 | ASHRAE 90.1-2007 EXTROOF IEAD CLIMATEZONE 2-8 | 0.3 | 0.273 | 0.283 | 39.14 | 0 | 7.39
SURFACE 43 | ASHRAE 90.1-2007 EXTROOF IEAD CLIMATEZONE 2-8 | 0.3 | 0.273 | 0.283 | 41.07 | 330.76 | 0
SURFACE 46 | ASHRAE 90.1-2007 EXTROOF IEAD CLIMATEZONE 2-8 | 0.3 | 0.273 | 0.283 | 36.99 | 31.87 | 0
Trombe Wall
Dencity | 150 | lb/ft3
Thickness | 8 | inches
Thermal Absorptance | 95 | %
Conductivity | 12 | Btu-in/ft2hR

## ground temperature
OS:Site:GroundTemperature:BuildingSurface,
{53760060-7d77-11e4-b4a9-0800200c9a66}, !- Handle
degC
Jan | 19.195
Feb | 19.191
Mar | 19.215
Apr | 19.25
May | 19.367
Jun | 20.429
Jul | 21.511
Aug | 21.776
Sep | 20.44
Oct | 19.538
Nov | 19.333
Dec | 19.237

## basecase
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 107.34 | 413.85 | 481.48
Net Site Energy | 30.94 | 119.3 | 138.8
Total Source Energy | 339.93 | 1310.67 | 1524.86
Net Source Energy | 97.99 | 377.83 | 439.57
End Uses
| Electricity [GJ] | Natural Gas [GJ] | Additional Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 49.34 | 0 | 0 | 0 | 0 | 0
Cooling | 9.18 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 28.82 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 17.92 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 2.07 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 107.34 | 0 | 0 | 0 | 0 | 0
Note: Electricity appears to be the principal heating source based on energy usage.
Window-Wall Ratio
| Total | North (315 to 45 deg) | East (45 to 135 deg) | South (135 to 225 deg) | West (225 to 315 deg)
Gross Wall Area [m2] | 463.1 | 156.52 | 108.93 | 92.47 | 105.18
Above Ground Wall Area [m2] | 463.1 | 156.52 | 108.93 | 92.47 | 105.18
Window Opening Area [m2] | 71.83 | 23.01 | 19.6 | 20.74 | 8.48
Gross Window-Wall Ratio [%] | 15.51 | 14.7 | 18 | 22.43 | 8.06
Above Ground Window-Wall Ratio [%] | 15.51 | 14.7 | 18 | 22.43 | 8.06
Window-to-Wall Ratio
| North | 14.7
| East | 18
| South | 22.43
| West | 8.06
| Total | 15.51

## comparison
| 18-reference-case | 17-naming
| Base Case | Radiant and Cooling Tower | Improved Envelope | As Designed | PV
Heating | 49.34 | 44.75 | 17.16 | 25.26 | 25.26
Cooling | 9.18 | 0.1 | 0.13 | 0.09 | 0.09
Interior Lighting | 28.82 | 28.82 | 28.76 | 10.88 | 10.88
Exterior Lighting | 0 | 0 | 0 | 0 | 0
Interior Equipment | 17.92 | 17.92 | 17.92 | 8.96 | 8.96
Exterior Equipment | 0 | 0 | 0 | 0 | 0
Fans | 2.07 | 0.03 | 0.03 | 0.02 | 0.02
Pumps | 0 | 0.26 | 0.1 | 0.16 | 0.16
Heat Rejection | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0
Total End Uses | 107.34 | 91.88 | 64.11 | 45.38 | 45.38
PV Production | 0 |  |  |  | 81.09
| Base Case | Radiant and Cooling Tower | Improved Envelope | As Designed | PV | 0
Cooling | 2549.9286 | 27.777 | 36.1101 | 24.9993 | 24.9993
Heating | 13705.5172 | 12430.5207 | 4766.6533 | 7016.647 | 7016.647
Interior Lighting | 8005.5331 | 8005.5331 | 7988.8665 | 3022.2138 | 3022.2138
Exterior Lighting | 0 | 0 | 0 | 0 | 0
Interior Equipment | 4977.7638 | 4977.7638 | 4977.7638 | 2488.8819 | 2488.8819
Exterior Equipment | 0 | 0 | 0 | 0 | 0
Fans | 574.9984 | 8.3333 | 8.3333 | 5.5555 | 5.5555
Pumps | 0 | 72.222 | 27.7777 | 44.4443 | 44.4443
Heat Rejection | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0
Total End Uses | 29816.5832 | 25522.1508 | 17808.2835 | 12605.5203 | 12605.5203
PV Produced | 0 | 0 | 0 | 0 | -22524.9369
22MWh = 1.8MWh/month
End Uses
| Electricity [GJ] | Natural Gas [GJ] | Additional Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 25.26 | 0 | 0 | 0 | 0 | 0
Cooling | 0.09 | 0 | 0 | 0 | 0 | 9.18
Interior Lighting | 10.88 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 8.96 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 0.02 | 0 | 0 | 0 | 0 | 0
Pumps | 0.16 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 45.38 | 0 | 0 | 0 | 0 | 9.18
Note: Electricity appears to be the principal heating source based on energy usage.